## BOQ for two Soakaway Wells
ANNEX D - BILL OF QUANTITIES Subject: Construction of 02 Soakaway wells Al Nao Hospital Omdurman Project: Omdurman Date: Apirl 15 2025
Project: Omdurman
Location: Al Nao Hospital
Description: Construction of 02 Soakaway wells - 40 meters deep (Depending on depth of Aquifer)
Contract Number:
# | Specification | unit | Quantity | Unit price (SDG) | total (SDG)
1 | Mobilization and Demobilization:
1.1 | Mobilization of equipment, materials, formworks and personnel to site, storage and demobilization on completion | Job | 1
2 | Excavation & Cartaway
2.1 | Excavate to make a circular hole with a diameter of 2.6 meters and a depth of 35 meters and the price includes removal of debris away from the site cart away | M3 | 371.462
2.2 | Excavate to make a circular hole with a diameter of 2.6 meters and a depth of 05 meters (depending on depth of Aquafar) and the price includes removal of debris away from the site cart away | M3 | 53.066
3 | Building work
The brickwork shall be constructed using grade one bricks, free of yellow bricks completely sealed from 0-17m and from 17-40m by pattern ''perforated brick wall with mortar joints''
3.1 | Supply and install first class-grade red brickwork with a thickness of 30 cm inside the soak pit, extending up to a height of 23 meters from the pit bottom, using a cement mortar mix of 1:3 (Cement to Sand) in accordance with the general technical specifications | M2 | 375.544
3.2 | Supply and Install first class-garde red brickwork with a thickness of 20 cm inside the soak pit, extending from a height of 17 meters to 40 cm above ground level, using a cement mortar mix of 1:3 (Cement to Sand), in accordance with the general technical specifications." | M2 | 277.576
4 | Concrete work
The price includes the necessary finishing work to achieve a smooth and clean external surface, as well as all materials required for the work, including cement, steel, and other necessary materials.
4.1 | Supply materials and cast reinforcement concrete 20 cm cover of well steel bars 16 mm distributing 15cm C/C both way double layer , concrete mix ratio 1:2:3 with steel cover ( manhole cover ) 45cm * 45 cm . | M3 | 2.826
5 | Backfilling
5.1 | Supply materials and back filling the space between the wall and lining use selected materials with good compaction . . | M3 | 50
6 | Modifications inside four Septic Tanks and connection to soakaway wells Indiviually
6.1 | • Close the existing walls of the chambers inside the existing septic tanks. • Install 6 FOG traps in each of the existing septic tanks. • Connect both existing septic tanks to a soakaway located 15- 20 meters away. Its include Supply materials and construct a 6-inch, 10-bar UPVC pipe drainage line, including the construction of 3-6 manholes (0.6m x 1.0 m) w*d . The work includes excavation, lining, plastering, and waterproofing, with the drainage system connected to the existing septic tanks and directly to the soakaway wells. | JOB | 2
Cost
Total Cost