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	[bookmark: _Hlk213061095]Plan International Sudan
White Nile Program
[bookmark: _Hlk213079436]Tender No. WNPA- PIS/PUZ/FY26/FRP/00022
Plan International – Sudan White Nile Program – Kosti Office would like to qualify Supply and Installation of Water and Chemical Dosing Pump Systems for Eddiuwaim Drinking water station in Edduweim localities.
[bookmark: _Hlk127780582] 
[bookmark: _Hlk145584464]Technical and financial offers are submitted by Supply and Installation of Water and Chemical Dosing Pump Systems to implement the tender as shown in accordance with the conditions and specifications specified in the tender below, as well as the tender brochure and documents, which will begin to be delivered to those wishing to be delivered as of Saturday 08th November 2025 from the organization's office in the White Nile, Kosti City During official working hours. The last day to withdraw the tender booklet for Supply and Installation of Water and Chemical Dosing Pump Systems is Thursday: 16th November 2025, and the last day to receive the envelopes from companies and contractors is Thursday: 20th November /2025 at ten in the morning, the following conditions shall be taken into account when submitting the bid:
1. The bidder must submit the financial offer in the local currency (Sudanese pound). 
2.  The submitted prices must be valid for a period of one month from the date of submitting the bid document. 
3.  The bidder must refer to the tender conditions and specifications before submitting. Any modification in the bid document that is not signed and stamped by the bidder deprives him of entry to the competition, and any error that is not signed or sealed is excluded from the competition. 
4.  The Bid Screening Committee has the full right to cancel the bid whenever it deems it necessary or for any other technical reasons that the Committee deems appropriate. 
5.  The person who is awarded the bid must meet with the committee to direct him to the technical authority and agree to supply the service according to the required conditions. 
6.  The bids shall be submitted in an envelope sealed with red wax and placed in the bids box at the organization's office in Kosti, Sarayat neighborhood, east of the Officers Club. 
7.  Please fill out the attached bidding brochure to unify bid specifications for all suppliers applying for competition, sign and seal (any bid that does not contain a completed bid notification will be excluded from the competition). 
8.  Please put the value of the value added tax and attach the assignment letter and a copy of the tax registration if you are assigned to collect it. 
9.  Signing the tender document means reviewing all the attached tender conditions and approving them. 
10.  Please put each bid document in a separate envelope and write the name of the bid clearly.
11. Tax Free party in the name of the Director of Plan International Sudan White Nile Program
12. The legal stamp within the limits of the cost of the bid (must be brought after the award of the bid to the successful party)
13. Certificate of discharge from Zakat in the name of the director of the organization
14. Business Name Registration Certificate
15. Certificate of financial ability (bank statement of at least three months)
16. Certificates of completion of similar works
17. Payment of 2% of the tender value by bank check, insurance company or bank guarantee letter in the name of the manager, supplemented to 10% for those who win the bid or refund for those who do not award the bid.
1. Attach a copy of the required documents (please do not attach any originals) and the documents are not returned إرفاق نسخة من المستندات المطلوبة (يرجى عدم إرفاق أي أصول) ولا يتم إرجاع المستندات
2. The tender brochure and specifications are obtained from the offices of Plan International – Sudan, the White Nile Program Office, Kosti, east of the Kosti Officers Club and south of the Sudanese Electricity Distribution Company.
 
	 


The last day to receive tender brochures from companies and contractors is, Thursday: 20th November /2025 at  (ten ) 10:00 AM in the morning
 at  (ten ) 10:00 AM in the morning
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السلام عليكم ورحمة الله تعالى وبركاته
السادة /  ...................................................................
                                   المحترم،،،،،،،
الأصناف و الكميات و المواصفات.
	clause

	Specifications
	Unit

	Quantity

	price

	Total

	1. 
	Provision and installation of Poly Allmonium Chloride (PAC) dosing pump injection Q48L/M, pressure 2 bar complete with all fittings & accessories and items and electric connection from the main Panel. 
توريد وتركيب طلمبة تجريع باك 48 لتر /دقيقة وضغط 2بار شاملة الملحقات ومعدات التوصيل والتحكم والكوابل الكهربائية مع التوصيل
	pump
	1
	
	

	2. 
	Provision and installation of Chlorin  dosing pump -Gaz  Q48L/M, pressure 10 bar complete with all fittings & accessories and items and electeric connection from the main Panel. 
توريد وتركيب طلمبة تجريع الكلور 48 لتر /دقيقة  وضغط 10 بار مع كامل التوصيلات والملحقات الكهربائية
	pump
	1
	
	

	3. 
	Provision and installation of water center fugal pumps capacity 500m3/h and total head 25m, NPSH=3m complete with all neccassary connection, the work shuold also include control Panel amtching with the motor power 75 KW and all protection parts to protect the motor. including fittings & Accessories :-
1- Main  Switch 160 Ampere
2- ccircuit Beraker 25 Ampere 2line,Main Contactor 75 Ampere,contactor delta 75 Ampere, Contactor Star 40 A, Over load 70 A,Timer star  & Delta,all devices are schneider brand, Protection  device(High & Low voltage,shortage & reverse surges)
3- 3 circuit Beraker 16 Ampere Indecater voltage & Ampere, Switch Operation & Stop , Cable 35 mm Reinforced 50 M length , Valve 10" Iron Core European,Valve 8" Iron Core European,Steel pipe 10" with 12 M length,steel pipe 8" with 12 M length.
4- Brand Caprary Made in Italy.
5- the installation of the pumps including the civil works.
ريد وتركيب طلمية طرد  مركزي مع الموتور بانتاجية 500 م3/ساعة وعمود رفع 25 متر مع كامل الملحقات والتوصيلات من شاسي وكوبلن ومفتاح تشغيل 75 كيلو واط  وكل اجهزة الحماية الخاصة  بالموتور وملحقات الطلمبة وكذلك مفتاح تامين رئيسي 160 امبير وسيركت بريكر 25 أمبير 2 خط وكنتاكتر رئيسي 75 أمبير وكنتاكتر دلتا 75 أمبير وكنتاكتر إستار 40 أمبير وأوفرلود 70 أمبير وتايمر إستار * دلتا كل الأجهزة ماركة إشنايدر وجهاز الحماية الرباعي و إرتفاع وإنخفاض الفولتية ونقص وعكس الفازات و3 سيركت بريكر 16 أمبير و مؤشرات الفولتية والأمبير مفاتيح  تشغيل وإيقاف كيبل 35 ملم مسلح بطول 50 منر بلف 10بوصة ذو قلب حديدي اوربي  المنشأ بلف 8 بوصة ذو قلب حديدي أوربي المنشأ ماسورة حديد 8 بوصة بسمك 5 ملي وطول 12 متر وماسورة حديد 10 بوصة سمك 5 ملي وطول 12 متر وجميع الملحقات من  بلف رداخ بحر ومسلوب وفلنشات وبلف رداخ عدم رجوع ووصلة صيانة لتركيب وتوصيل الطلمبات ماركة كبراري ايطالية المنشأ
تشمل التركيب اعمال المدنية خسب اصول الصنعة
	pump
	1
	
	

	4. 
	Provision and installation of water center fugal pumps capacity 300m3/h and total head 70m, NPSH=3m complete with all neccassary connection, the work shuold also include control Panel amtching with  motor  power 110 KW and all protection parts to protect the motor including fittings & accessories :-
1-  Main  Switch 250 Ampere
2- ccircuit Beraker 25 Ampere 2 line,Main Contactor 110 Ampere ,contactor delta 110 Ampere, Contactor Star 65 Ampere, Over load 110 A,Timer star  & Delta,all devices are schneider brand, Protection  device(High & Low voltage,shortage & reverse surges)
3- 3 circuit Beraker 16 Ampere Indecater voltage & Ampere, Switch Operation & Stop , Cable 50 mm Reinforced 50 M length , Valve 10" Iron Core European,Valve 8" Iron Core European,Steel pipe 10" with 12 M length,steel pipe 8" with 12 M length
4- Brand Caprary Made in Italy
توريد وتركيب طلمية طرد  مركزي مع الموتور بانتاجية 300 م3/ساعة وعمود رفع 70 متر مع كامل الملحقات والتوصيلات من شاسي وكوبلن ومفتاح تشغيل 110 كيلو واط  وكل اجهزة الحماية الخاصة  بالموتور وملحقات الطلمبة وكذلك مفتاح تامين رئيسي 250 امبير وسيركت بريكر 25 أمبير 2 خط وكنتاكتر رئيسي 110 أمبير وكنتاكتر دلتا 110 أمبير وكنتاكتر إستار 65 أمبير وأوفرلود 110 أمبير وتايمر إستار * دلتا كل الأجهزة ماركة إشنايدر وجهاز الحماية الرباعي إرتفاع وإنخفاض الفولتية ونقص وعكس الفازات و3 سيركت بريكر 16 أمبير و مؤشرات الفولتية والأمبير و مفاتيح  تشغيل وإيقاف كيبل 50 ملم مسلح بطول 50 منر بلف 10بوصة ذو قلب حديدي اوربي  المنشأ بلف 8 بوصة ذو قلب حديدي أوربي المنشأ ماسورة حديد 8 بوصة بسمك 5 ملي وطول 12 متر وماسورة حديد 10 بوصة سمك 5 ملي وطول 12 متر وجميع الملحقات من  بلف رداخ بحر ومسلوب وفلنشات وبلف رداخ عدم رجوع ووصلة صيانة لتركيب وتوصيل الطلمبات ماركة كبراري ايطالية المنشأ
	pump
	1
	
	

	المجموع
	

	VAT  %  قيمة الضريبة اذا مكلف بتحصيلها مع ارفاق خطاب التكليف
	

	الإجمالي
	




الجملة كتابتاً ...........................................................................................
الفترة الزمنية لتسليم  المشروع: .......................................................

قسم المشتروات:   محمد عبدالقادر محمود          التوقـــــيع ………………………................     الختم ...................................
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