# Detailed Technical Specifications(ALTHORA CENTER)

### 1. Doors and Windows

Material: Galvanized steel sheet 1.2 mm thick, anti-rust, corrosion-resistant.

Frame: 40×40×1.5 mm steel square tubes.

Finish: Primer + two coats  paint.

Accessories: Heavy-duty hinges, steel handle, double key lock.

Installation: Anchored with expansion bolts, aligned per drawings.

### 2. Zinc Structure Pipes

Galvanized rectangular pipes 4×8 cm, thickness 1.5 mm.

Frames for walls and roofs

Installed with a slope of 3–5% for rainwater drainage.

Painting: primer + two coats paint.

Welding: Full welds, ground smooth, anti-rust coated.

## 3.EPX Thermal Insulation

- Thickness 3 cm, resistant to heat and humidity.

- Installed directly beneath the zinc sheets.

- Fixed with special adhesive tape to ensure stability and prevent heat leakage.

- Installation according to specifications and under engineer supervision.

## 4.Screws and Rubber Gaskets

- Used for fixing metal sheets and insulation.

- Properly distributed over all sections to prevent leakage.

- Installation according to specifications and under engineer supervision.

### 5. Wood Specification

Type: Water-resistant plywood – Grade A.

Thickness: 20 mm Minimum,

Treatment: moisture-proof paint

Application: Interior wall ,roof

## 6. Electrical Works (Cables & Installations)

Conduits & Fittings:
All internal wiring shall be concealed in rigid PVC conduits, heavy-duty type, minimum diameter 20 mm, compliant with BS EN 61386.
External connections to be routed in ½” cloth-braided rubber casing, fully weather-sealed.

Cables:
Type: Copper conductor, single-core, PVC insulated, 450/750V, conforming to IEC 60227.
Minimum size: 2.5 mm² for socket outlets, 6 mm² for main supply.
All cables shall bear manufacturer identification, voltage rating, and batch number.

Switches & Sockets:
Type: Heavy-duty, white plastic or bakelite, rated 13A, 250V.
Installation height: Switches at 1.4 m, sockets at 0.4 m above finished floor level.

Lighting Fixtures:
Energy-efficient LED luminaires, IP-65 for outdoor, IP-44 for indoor.
Ceiling or wall-mounted according to drawings, with proper earthing connection.

Distribution Board:
Type: Surface-mounted, lockable, with labeled MCBs.
Each circuit must be protected by 10A–32A MCBs and a 30mA RCD for safety.

## 7. Plumbing Works (Water Supply & Drainage)

- Pipes:
Type: cloth-braided rubber hoses for main lines, PPR (Polypropylene Random Copolymer) for internal connections.
Sizes: Main line 1”, internal supply ½”, waste 1½” to 2” depending on fixture.

Fittings:
Use threaded brass or compression-type joints.
All fittings must be from approved brands with matching pressure class.

Valves:
Ball valves, full bore, brass or bronze, PN16 pressure rating.
One valve at each service point (kitchen, bathroom).

- yard points.

measuring 2×1.5×1 meter
    Construction of square benches, finished with 2 cm plaster coating and drainag system.

- Fixtures:
Chrome-plated brass faucets for sinks and yard points.
PVC traps and waste outlets with removable caps for cleaning.

Testing:
Water supply system tested at 6 bar for 1 hour, with no pressure drop.
Drainage system tested for leaks and proper slope (1–2%).

- Eng: Asim Sedig Tambal

- Signature