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خدمات الاغاثة الكاثوليكية  CRS 
Madani OfficeNorth Sudan Program

طلب عرض أسعار
Request for Quotation

Name of Supplier: ___________________________________________إسم العميل:
Address: ______________________________________________________العنوان:
Contact Person: __________________________________________إسم المسئول المباشر:
Phone/ Email: _____________________________________: رقم الهاتف والبريد الالكتروني 
[bookmark: _Hlk159666076]Date of RFQ 15 of December –2025     
RFQ No: CRS-MAD-SD6257-2025                           
	Bank details:

· Bank Name: …………………………………………………...

· Bank account name: …………………………………………


· Bank number ………………………………………………...

· Branch: ………………………………………………………...


	تفاصيل الحساب:

   إسم الينك: ---------------------------------------

 اسم الحساب:--------------------------------------

  رقم الحساب :  -----------------------------------
  
  الفرع --------------------------------------------------



Specifications: - 
	Description of Items
وصف القطع المطلوبه
	Arabic
الوصف باللغة العربية
	Units Needed
العدد
	Price per Day
In SDG
	

Total Price in SDG

	 Generator Shelter as per below specifications 
	2
	
	

	ATS for generator 150KVA as per below specification 
	2
	
	

	Fuel storage with raising pump as per below specifications
	2
	
	

	Total

	



	Subject:
	Provision of Generator shelter, ATS and Fuel storage tank  

	Date of this RFQ:
	15 December, 2025

	Closing Date for Receipt RFQ
	25th December 2025 at 4:00 P.M

	Submission Address
	House No.366, Block 4, Hay Almatar, East Al-Waledain Mosque, Alsilk Street, Port Sudan OR House No. 17, Block 289, Hay Zamalek, in the city of Madani Al-Kubra

	Submission Email
	tenders.sudan@crs.org

	Reference No.:  
	CRS-MAD-SD6257-2025                           




Scope of Work:                                                             

Generator shelter specification 
	No
	Shelter/ATS/Fuel storage 
	Specifications 

	1
	Generator shelter 
	The generator shelter will be constructed using durable iron materials to protect the generator from weather conditions and unauthorized access. The structure will include a strong iron frame, corrugated iron sheet walls and roof, lockable access door, and adequate ventilation openings to ensure proper airflow and cooling during operation. The shelter will be painted with anti-rust coating for long-term durability and weather resistance
· Structure: Welded iron frame with corrosion-resistant coating.
· Walls: Stainless steel wire mech fixed on the frame with bolts and washers.
· Roof: Sloped corrugated iron roof with rainwater drainage provision.
· Floor: Concrete base with vibration-damping pads for generator placement.
· Door: Lockable iron door for security access.
· Ventilation: Louvered openings or mesh vents on both sides for airflow.
· Exhaust: Dedicated outlet for generator exhaust pipe with heat protection.
· Paint: Anti-rust primer and weather-resistant paint for all metal surfaces.
Dimensions: Sized to fit generator 150KVA set with minimum 1 meter clearance on all sides for maintenance

	2
	ATS
	Automatic Transfer Switch (ATS) – Specifications for 150 kVA Generator
1. Capacity:
· Rated for 150 kVA generator (approximately 144 A at 400V, 3-phase, 50Hz).
· Must be sized at least 125% of generator full load current for safety and durability.
2. Type:
· Automatic Transfer Switch (ATS), 4-pole, 3-phase + Neutral.
· Electrically and mechanically interlocked to prevent simultaneous source connection.
3. Voltage & Frequency:
· Rated Voltage: 400/230V AC, 50Hz.
· Control Voltage: 220–240V AC (or as per generator control system).


	3
	Storage Tank with Raising pump
	Fuel Storage Tank System – 3,000 Liters Capacity
1. Capacity:
· Nominal capacity: 3,000 liters (diesel storage)
· Effective usable capacity: Minimum 95% of total volume
2. Tank Construction:
· Material: Mild steel (minimum 3 mm thickness) or stainless steel welded and pressure tested.
· Type: Above-ground horizontal cylindrical tank with support stand.
· Fittings: Inlet, outlet, drain, vent, and fuel level gauge.
· Finish: Exterior coated with anti-rust primer and weather-resistant paint.
· Inspection manhole with bolted cover.
· Bund wall or containment tray (minimum 110% tank capacity) for environmental protection.
3. Fueling System Components:
· Fuel Transfer Pump:
· Type: Electric pump, self-priming.
· Capacity: 40–60 liters per minute (minimum).
· Power supply: 220–240V AC (single phase) or 12/24V DC if connected to generator system.
· With built-in strainer and non-return valve.
· Fuel Hose and Nozzle:
· Hose: Heavy-duty rubber or composite fuel hose, length 5–10 meters.
· Nozzle: Automatic shut-off fuel nozzle with swivel connection.
· Fuel Filter:
· Inline fuel filter/water separator to ensure clean fuel supply to generator.
· Fuel Meter 
· Digital or mechanical flow meter showing total and batch volume dispensed.
4. Accessories:
· Fuel level indicator (gauge or sight glass).
· Emergency shut-off valve and venting system.
· Lockable fill point to prevent unauthorized access.
· Earthing connection for safety.








	Disclaimer Clause: We declare that we have read all the terms & conditions and the information provided by our company are correct and incase of any deviation from the quoted price or terms & condition we will inform CRS accordingly.                      
	مناط المسئولية: بهذا نقر باننا قد اطلعنا علي كافة الشروط  والمطلوبات وان المعلومات المقدمه من الشركة صحيحة , وفي حالة اي اختلاف عن العرض المقدم من قبلنا , فاننا سوف نقوم باخطار منظمة الاغاثة الكاثوليكية بذلك.





	Name
الاسم 
	Signature with company Stamp
التوقيع والختم

	Date: --------------


التأريخ:----------------

	
	
	 
	
	
	
	 

	 Closing Date of Tender: 25/12/2025 at 04:00 PM 
Please mention "Quotation submitted for the Supply of AAA By BBB Company" on sealed envelope. يلزم تسليم العطاء في مظروف مغلق ومختوم وكتابة : عرض اسعار مقدم عن مناقصة :::::::::: والمقدمة من ::::::::::::::::

	
Sealed quotation must be received in CRS Office not later than: 
عرض الاسعار يجب ان يقدم  في تأريخ لا يتجاوز

	

لفترة أسبوع فقط
	 





	For any queries, feel free to contact us through above mentioned contact details. 

لاي استفسار , الرجاء عدم التردد في الاتصال بالرقم المرفق/ 0912284670
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