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	[bookmark: _Hlk213061095]Plan International Sudan
White Nile Program
[bookmark: _Hlk213079282]Tender No. WNPA- FY26-02
[bookmark: _Hlk215995884][bookmark: _GoBack]Plan International – Sudan White Nile Program – Kosti Office would like to invite you to apply of Supply of materials and Installation of a compact unit water treatment with a capacity of 30 m3/h in the Al-Fashashoyah area, Guli locality, White Nile State , Sudan.
[bookmark: _Hlk127780582] 
[bookmark: _Hlk145584464]Technical and financial offers are submitted by  supply of materials and Installation of a compact unit water treatment with a capacity of 30 m3/h in the Al-Fashashawiya area, Quli locality, White Nile State , Sudan to implement the tender as shown in accordance with the conditions and specifications specified in the tender below, as well as the tender brochure and documents, which will begin to be delivered to those wishing to be delivered as of Wednesday 17th December 2025 from the organization's office in the White Nile, Kosti City During official working hours. The last day to withdraw the tender booklet for  supply of materials and Installation of a compact unit water treatment with a capacity of 30 m3/h in the Al-Fashashawiya area, Quli locality, White Nile State , Sudan last day of tender book withdrawal from organization is Sunday 28th December 2025, and the last day to receive the envelopes from companies and contractors is Wednesday: 31th December 2025 at ten in the morning, the following conditions shall be taken into account when submitting the bid:
1. The bidder must submit the financial offer in the local currency (Sudanese pound). 
2.  The submitted prices must be valid for a period of one month from the date of submitting the bid document. 
3.  The bidder must refer to the tender conditions and specifications before submitting. Any modification in the bid document that is not signed and stamped by the bidder deprives him of entry to the competition, and any error that is not signed or sealed is excluded from the competition. 
4.  The Bid Screening Committee has the full right to cancel the bid whenever it deems it necessary or for any other technical reasons that the Committee deems appropriate. 
5.  The person who is awarded the bid must meet with the committee to direct him to the technical authority and agree to supply the service according to the required conditions. 
6.  The bids shall be submitted in an envelope sealed with red wax and placed in the bids box at the organization's office in Kosti, Sarayat neighborhood, east of the Officers Club. 
7.  Please fill out the attached bidding brochure to unify bid specifications for all suppliers applying for competition, sign and seal (any bid that does not contain a completed bid notification will be excluded from the competition). 
8.  Please put the value of the value added tax and attach the assignment letter and a copy of the tax registration if you are assigned to collect it. 
9.  Signing the tender document means reviewing all the attached tender conditions and approving them. 
10.  Please put each bid document in a separate envelope and write the name of the bid clearly.
11. Tax Free party in the name of the Director of Plan International Sudan White Nile Program
12. The legal stamp within the limits of the cost of the bid (must be brought after the award of the bid to the successful party)
13. Certificate of discharge from Zakat in the name of the director of the organization
14. Business Name Registration Certificate
15. Certificate of financial ability (bank statement of at least three months)
16. Certificates of completion of similar works
17. Payment of 2% of the tender value by bank check, insurance company or bank guarantee letter in the name of the manager, supplemented to 10% for those who win the bid or refund for those who do not award the bid.
1. Attach a copy of the required documents (please do not attach any originals) and the documents are not returned إرفاق نسخة من المستندات المطلوبة (يرجى عدم إرفاق أي أصول) ولا يتم إرجاع المستندات
2. The tender brochure and specifications are obtained from the offices of Plan International – Sudan, the White Nile Program Office, Kosti, east of the Kosti Officers Club and south of the Sudanese Electricity Distribution Company.
 
	 


The last day to receive tender brochures from companies and contractors is, Wednesday: 31th December /2025 at  (ten ) 10:00 AM in the morning




17th December.2025                                                                                                                    Reference WNPA- FY26-02

السادة /  ...................................................................
                                   المحترم،،،،،،،
السلام عليكم ورحمة الله تعالى وبركاته
Bill of quantity for supply of materials and Installation of a compact unit water treatment with a capacity of 30 m3/h in the Al-Fashashawiya area, Guli locality, White Nile State , Sudan.

	Total 
	Unit Price 
	Quantity 
	UoM
	Description and Specifications
	#

	أعمال تخطيط وتنظيف الموقع SITE CLEARANCE       
	1

	
	
	1
	Job
	Site cleaning and planning, including removal of all obstacles to the water treatment plant site and leveling to the natural ground level.
تنظيف وتخطيط الموقع شامل إزالة كل العوائق لموقع محطة المعالجة مع التسوية حسب مستوي الأرض الطبيعية
	1.1

	أعمـــــــــــــــال الأساسات EXCAVATION AND DISPOSAL                   
	2

	
	
	
72
	
M3
	Excavation starting from existing ground level including leveling and ramming bottom, and removal of surpluses caveated material  from cleared site for dimension 12*5 with depth 1.2  Supervising Engineer's Instructions.
حفر أساسات محطة معالجة المياه مع إزالة ناتج الحفر بعيدا عن الموقع بأبعاد 5*12 بسمك 1.2 متر وحسب التصميم المرفق وحسب توجيهات الإشراف
	2.1

	
	
	
120
	
M3
	Supply materials and backfill in pits selected fill material successive layers each layer watered and well compacted according to Supervising Engineer's Instructions.
توريد مواد وعمل ردميات من الحماري (تربة إحلال) تحت القاعدة الحصيرية مع الدمك الجيد والتسوية بمندالة وحسب الرسومات المرفقة وتوجيهات المهندس المشرف.
	2.2

	
	
	
60
	
M3
	Supply material and construct P.C  slap for foundation base12x5x.10m , concrete mix 1:3:6
توريد مواد وعمل خرسانة عادية سمك 10سم بأبعاد 5*12 متر بخلطة 1:3:6 وحسب الرسومات الموضحة
	2.3

	
	
	
29
	
M3
	Provision & installation and cast Reinforced Concrete; Grade 30N/mm², rate to include beams, shuttering, and reinforcement.
توريد وتشييد خرسانة مسلحة لقاعدة المحطة المدمجة بخلطة 1:1.5:3 أساس حصيري شامل الأبيام حسب الرسوم التوضيحية لأبعاد وقطر السيخ
	2.4

	WATER TREATMENT PURIFICATION UNIT         وحدة معالجة المياه           
	3

	
	
	1
	Number 
	Flash Mixer: provision manufacture, and installation of a flash mixing tank for adding acoagulations.The tank will be constructed of 8mm thickness sheet iron for the base and 6mm thickness sides, with dimensions of 2*1*1 meters. This includes all equipment such as a motor, gearbox, and everything necessary to complete the work. Interior painting will be done with a potable water-safe epoxy, and exterior painting with deluxe paint, according to the attached drawings and specifications. The tank will also include European valves with iron fittings, according to the diameters shown in the design.
الخلاط السريع : توريد مواد وتصنيع وتركيب حوض خلط سريع للمياه الخام لإضافة المروب من الصاج حديد سمك 8 ملي للقاعدة والجوانب سمك 6 ملي بأبعاد 1*1*2 متر شامل كل المعدات من موتور وجربوكس وكل ما يلزم لإكمال العمل واعمال الدهانات من الداخل بمادة ايبوكسية صالحة لمياه الشرب ومن الخارج ببهية ديلوكس حسب الرسومات والمواصفات المرفقة شاملة البلوفة أوربية المنشأ ذات صمام حديدي الأقطار الموضحة بالتصميم المرفق
	3.1

	
	
	3
	Number
	Rapid Mixer: provision materials manufacture, and installation of a rapid raw water mixing tank for adding a coagulations .The tank will be constructed of 8mm thickness sheet iron for the base and 6mm thickness sides, with dimensions of 2*1*0.65 meters. This includes all equipment & accessories and everything necessary to complete the work. Interior painting will be done with a potable water-safe epoxy, and exterior painting with deluxe paint, according to the attached drawings and specifications. The tank will also include European valves with iron fittings, according to the diameters shown in the design
حوض الخلط البطيء: توريد مواد وتصنيع وتركيب حوض خلط بطيء من الصاج حديد سمك 8 ملم للقاعدة الجوانب سمك 6 ملم بأبعاد 2*1*0.65 شامل كل الملحقات وأعمال الدهانات من الداخل بمادة إيبوكسية صالحة لمياه الشرب ومن الخارج ببوهية ديلوكس وكل ما يلزم لإكمال العمل حسب الرسومات والواصفات المرفقة شامل البلوفة أوربية المنشأ ذات صمام حديدي حسب الأقطار الموضحة بالتصميم

	3.2

	
	
	1
	Number
	Sedimentation basine: provision materiales manufacture, and installation of a sedimentation tank will be constructed of 8mm thickness sheet iron for the base and 6mm thickness sides, with dimensions of 3*6*3 meters. This includes all equipment & accessoriess and everything necessary to complete the work. Interior painting will be done with a potable water-safe epoxy, and exterior painting with deluxe paint, according to the attached drawings and specifications. The tank will also include European valves with iron fittings, according to the diameters shown in the design
حوض الترسيب: توريد مواد وتصنيع وتركيب حوض الترسيب بأبعاد 3*6*3 متر من الصاج حديد 8 ملم للقاعدة والجوانب سمك 6 ملم شامل عمل الشدادات والدعامات اللازمة حسب ما موضح في التصميم المرفق مع أعمال الدهانات من الداخل بمادة إيبوكسية صالحة لمياه الشرب ومن الخارج ببوهية ديلوكس شامل البلوفة أوربية المنشأ ذات صمام حديدي حسب الأقطار الموضحة بالتصميم
	3.3

	
	
	1
	Number 
	Filter Media : provision materiales & manufacture and installation of a filter tank .The tank will be constructed of 8mm thickness sheet iron for the base and 6mm thickness sides, with dimensions of 2*3 meters. This includes all equipment This includes all equipment & accessoriess and everything necessary to complete the work. Interior painting will be done with a potable water-safe epoxy, and exterior painting with deluxe paint, according to the attached drawings and specifications. The tank will also include European valves with iron fittings, according to the diameters shown in the design
الفلتر الرملي السريع: توريد مواد وتصنيع وتركيب خزان فلتر رملي سريع بأبعاد 3*2 متر من الصاج حديد سمك 8ملم للقاعدة والجوانب سمك 6ملم شامل عمل المواسير الداخلية للفلتر ولعملية الغسيل العكسي ومواسير التصريف والفائض اللازمة مع أعمال من الداخل بمادة إيبوكسية صالحة لمياه الشرب ومن الخارج ببوهية ديلوكس وحسب ما موضح في التصميم المرفق شامل البلوفة أوربية المنشأ ذات صمام حديدي حسب الأقطار الموضحة بالتصميم وحسب توجيهات المهندس المشرف   
	3.4

	
	
	1
	M3
	Sand filter media: Supply, installation, and arrangement of graded gravel and sand with good cleanliness as shown in the attached design.
مواد الفلتر الرملي: (Filter media) توريد مواد وتركيب وترتيب حصي ورمل مدرج مع النظافة الجيدة وحسب ما موضح في التصميم المرفق
	3.5

	
	
	6
	M3
	Railings and walkway: Supply of materials and construction of a comprehensive walkway and handrdrail as shown in the attached design. 
الدرابزين والمدرج: توريد مواد وعمل مدرج وممشي شامل حواجز الحماية حسب ما موضح في التصميم المرفق
	3.6

	
	
	1
	Job
	Drainage system: provision materials and construction of a red brick drainage system for all parts of the integrated watertreatment  including the supply and installation of a drainage valve according to the attached drawings and the instructions of the supervising engineer
. نظام التصريف: توريد مواد وعمل نظام تصريف من الطوب الأحمر لكامل أجزاء المحطة المدمجة مع توريد وتركيب بلوفة التصريف حسب الرسومات المرفقة وتوجيهات المهندس المشرف
	3.7

	
	
	1
	Number
	Provision and installation of Poly Allmonium Chloride (PAC) dosing pump injection Q48L/M, pressure 2 bar complete with all fittings & accessories and items and electeric connection from the main Panel. 
توريد وتركيب طلمبات تجريع الباك48 لتر /دقيقيه ضغط 2 بار شامل معدات التوصيل والتحكم والكوابل وملحقاته الكهربائية
	
4

	
	
	1
	Number 
	Provision and installation of Chlorin  dosing pump -Gaz  Q48L/M, pressure 10 bar complete with all fittings & accessories and items and electeric connection from the main Panel. 
توريد وتركيب طلمبات تجريع الكلور48 لتر /دقيقيه ضغط 210بار شامل معدات التوصيل والتحكم والكوابل وملحقاته
	5

	
	
	1
	Number 
	Provision and installation of water pumps capacity 30m3/h and total head 25m,complete with all neccassary connection, the work shuold also include control Panel amtching with  motor  power and all protection parts to protect the motor including fittings & accessories : all devices are schneider brand or italy, Protection  device(High & Low voltage,shortage & reverse surges) 
توريد وتركيب طلمبات طرد مركزي بإنتاجية 30م3/س بعمود رفع 25 متر مع كامل التوصيلات الهيدروليكية (بلف رداخ سحب مع الحماية من الحشائش ــ بلف عدم رجوع ــ وصلة فك وتركيب ــ جهاز قياس الضغط ــ جهاز قياس التصرف ــ توصيلات السحب ــ الرمي) وشامل التوصيلات الكهربائية مفتاح تحكم شامل الشاسي والقاعدة الخرسانية أجهزة الحماية والكوابل من المفتاح الرئيسي إلي مفتاح التحكم إلى الطلمبة أوربية المنشأ
	6

	
	
	1
	Number
	Provision and installation of water pumps capacity 30m3/h and total head 50m, complete with all neccassary connection, the work shuold also include control Panel amtching with  motor  power and all protection parts to protect the motor including fittings & accessories : all devices are schneider brand or italy, Protection  device(High & Low voltage,shortage & reverse surges)  European. 
توريد وتركيب طلمبات طرد مركزي بإنتاجية 30م3/س وعمود رفع 50 متر مع كامل التوصيلات الهيدروليكية (بلف رداخ سحب ــ بلف عدم رجوع ــ وصلة فك وتركيب- جهاز قياس الضغط ــ جهاز قياس التصرف ــ توصيلات السحب ــ الرمي) وشامل التوصيلات الكهربائية مفتاح تحكم شامل الشاسي والقاعدة الخرسانية أجهزة الحماية والكوابل من المفتاح الرئيسي إلي مفتاح التحكم إلى الطلمبة أوربية المنشأ
	7

	
	
	1
	Number
	supply and installation of a 15m³ air compressor at 2 bar pressure, including electrical and hydraulic accessories, including connecting pipes and fittings (European-made knife valves, flanges, elbows) to European-made filter tanks
توريد وتركيب ضاغط هواء بسعة 15م3 ضغط 2 بار شامل الملحقات الكهربائية والهيدروليكية شامل مواسير التوصيلات والملحقات (بلوفة سكينة اوربية المنشأ- فلنشات- اكواع) الي أحواض الترشيح أوربي المنشأ
	8

	
	
	
	
	المجموعSub Total                        
	

	
	
	
	
	VAT  %  قيمة الضريبة اذا مكلف بتحصيلها مع ارفاق خطاب التكليف
	

	
	
	
	
	الإجماليTotal                                 
	












الجملة كتابتاً بالاحرف .........................................................................................
الفترة الزمنية لتنفيذ و تسليم  المشروع: .......................................................

قسم المشتروات:   محمد عبدالقادر محمود      التوقـــــيع ……………................     الختم ...................................

اسم العمل / الشركة : ........................................... 
التوقيع :..............................................................
الختم :................................................................
التلفون :.....................................................................
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