## Kandowa Water Rehabilitation
BOQ Kandowa Piped Water Supply Rehabilitation – Nyala Town, South Darfur”
Item Description | Unit | Quantity | Unit Cost | Amount Cost
Sub-total cost
Mobilization and demobilization of all required equipments, tools, machinery and personel at site. | Site | 1
Borehole cleaning and development | Borehole | 2
Pumps, Control Panels and Electrical(Kondowa and Al- fania Water Systems)
Supply and install a Grundfos pump (SP 18-7) and Grundfos pump inverter RSI 7.5 KW with all accesssorries for protections as specified in inverter manual including mounting board and others | Set | 1
Supply and install a Grundfos pump (SP 18-7 and SP 18-5) and Grundfos pump inverter RSI 11 KW with all accesssorries for protections as specified in inverter manual including mounting board and others | Set | 4
BBG 35 mm aluminum cable | Meter | 4000
Electrical accessories (connectors, panels, switches) | station | 1
Solarization of Six Boreholes ( 11Kw x 6 Bore holes = 66Kw) including Solar mounting structures and accessories, Includes solar array, pump inverter, mounting structures, combiner boxes, wiring, lightning protection Kondowa water system.
Supply and install Monocrystalline PV Module (Ameri solar) with Maximum Power at STC(Pmax) - 660W, Open-Circuit Voltage (Voc)- 49.8V, Short-Circuit Current (Isc)-13.9A, Rated output (Pmpp)- 660W, rated current (Impp)-10.48A, Rated Voltage (Vmpp)-42.10V Includes solar array, mounting structures, combiner boxes, wiring, lightning protection. | Pc | 186
Supply and installed a complete Single-Arm 6 meter Aluminium pole Street Light , 200watts with photocell sensor | Pc | 12
Supply and install Surge Protection DC- Device ABB-OVR T2 40-150 P U or DEHNguard or Phoenix(VAL-MS 60/FM Plug & box 15kA) | Pc | 6
Supply and install Earth rod 2m and above and grounding accessories, including Clamps, lugs etc | Pc | 6
Supply and install Spike lightining arrestor 5m free from the ground casted by concrete grade 20 | Pc | 6
Solarization of One Bore hole( ( 7.5Kw x 1 Bore hole = 7.5Kw) including Solar mounting structures and accessories, Includes solar array, pump inverter, mounting structures, combiner boxes, wiring, lightning protection (Kondowa water system).
Supply and install Monocrystalline PV Module (Ameri solar) with Maximum Power at STC(Pmax) - 660W, Open-Circuit Voltage (Voc)- 49.8V, Short-Circuit Current (Isc)-13.9A, Rated output (Pmpp)- 660W, rated current (Impp)-10.48A, Rated Voltage (Vmpp)-42.10V Includes solar array, mounting structures, combiner boxes, wiring, lightning protection. | Pc | 22
Supply and installed a complete Single-Arm 6 meter Aluminium pole Street Light , 200watts with photocell sensor | Pc | 1
Supply and install Surge Protection DC- Device ABB-OVR T2 40-150 P U or DEHNguard or Phoenix(VAL-MS 60/FM Plug & box 15kA) | Pc | 1
Supply and install Earth rod 2m and above and grounding accessories, including Clamps, lugs etc | Pc | 1
Supply and install Spike lightining arrestor 5m free from the ground casted by concrete grade 20 | Pc | 1
Pipelines , Masonery and Fence works
HDPE pipeline PN 16 8inch inspection and maintenance | Meter | 100
Construction of solar stands 1m Depth with Concrete Grade 20 ( 1:2:4) for Kondowa
provision and mark up solar stand site | Job | 1
provision and excavate solar stand foundation with 400mmx400m depth 600mm | Foundation | 115
Provision and fabrication of Plain concrete in 1:3:6 rate ,400x400mmx600mm(400mm under ground and 200mm above GL) as solar stand columns foundation watering will be used 3times/day/4day. | Foundation | 115
provison and fabrication U.beman 120x60mmx6mm thickness as columns with 2.5m at front and 1.8m at back to make 15degree, the columns will be fixed using plain concrete as mentioned in items above fixing of columns with PC suppose to raise above ground level 20cm at ,watering will be used 3time/day/4day. | column | 115
provision and lay 2.5",6mm thickness equal iron angles on the top of solar stand in the direction width and longitudenal ways using high weld to fix the angles , the cost includes painting 3 faces at least. | PCs(6m equal iron angles) | 122
Provision and fabrication of 2" ,5mm thickness equal iron angles to cover solar cells for all sites of the cells using high weld to fix solar cell. | PCs(6m equal iron angles) | 122
Provision and painting of solar stand using selected color | job | 1
Supply and fix donor signpost ( Size 1.5m x 2.5m) as Per Project Manager recommendation and Guidance | Signboard | 1
Supply and fix an engraved marble stone at each station with BH specifications, including donor logos (size: 0.5 m × 0.5 m), as per the Project Manager’s recommendation and guidance | Signboard | 1
Total