## BoQ
HA - Sudan
BOQ for Construction of one water yard equipped with a solar power system in Al Rogla Hamad and Wad Al Shafie villages South Al Jazeera.
Mobilization, drilling , and installation
# | Items | Unit | Quantity | Unit Cost (SDG) | Total Cost SDG
1 | Mobilization of equipment, personnel and construction materials , The item is inclusive of site clearing and levelling. | Lum sum | 2 |  | 0
2 | Detailed geological investigations will be conducted, including a review of existing borehole data in Al Rogla Hamad and Wad Al Shafie villages. Based on the findings, a new production well will be drilled to the depth recommended by the project geologist. Drilling will be carried out using a rotary or combined drilling rig. Shallow formations will be drilled to install conductor casing and stabilize the upper layers. A drilling bit with a diameter of 12.5–14 inches will be used during the drilling process. A complete lithological log and well completion report will be prepared after drilling. The scope of work includes well drilling, installation of UPVC or steel (STM) casing of 8-inch diameter with a pressure rating of 10 bar or more, and a screen of the same diameter and specification with a length of 80–100 feet. The estimated cost is based on an expected drilling depth of approximately 350–400 feet. | well | 2 |  | 0
3 | Carry out, constant rate pumping test for 12- 24 hours including continuous measurement of discharge rate, static water level, dynamic water level, recovery monitoring, and determination of safe sustainable yield. Step drawdown pumping test (minimum three steps, 60 minutes each) including calibrated discharge measurement, and prepare a technical report and share it accordingly. | job | 2 |  | 0
4 | Supply construction materials and carry out borehole development and the cost includes, construct well neck and platform for area of 2 m width *2 m long* 0.1 m thickness. | job | 2 |  | 0
5 | Supply materials (HDPE pipe 3 inch and two inches with all junctions and fittings including reducer 4" and 3 " non return valves and Heavey duty valve needed size and carry out plumbing of conveyance system and connected with existing water network, each site 50 m distance. | site | 2 |  | 0
| Sub total for drilling and installation |  |  |  | 0
The line include supply and install solar power system
6 | Provide and installation of Inverter Motor 11 KW, 380 Rated Output Power 11kw,( VFD, equivalent to VEICH type), Absolute DC input voltage between (380~415 v), Output Wave Pure Sine Wave Rated Output Voltage 380V/3ph AC Output Frequency 50-60 Hz Working Efficiency>98% Harmonic distortion is less than 3%. Warranty after installation should be for 5 years at least for the inverters. (the inverter can size can modify base on pumping test result). | PCS | 2 |  | 0
7 | Supply and installation of Solar Panel equivalent to Jinko 710 Watt, Power output (W) 710 W, Cell Type equivalent to mono-crystalline or polycrystalline, Operating PV temperature ranges between -10 °C & + 85 °C., Module Efficiency shall be at least 19%. The PV module frame should be made from Anodized Aluminium. The Photovoltaic modules should be manufactured recently. The warranty for module defects after installation should be at least 20 years. The awarded Proposer shall provide a manufacturer's power guarantee for all PV modules that will be installed with their serial numbers, which guarantees that the loss of the output is not more than 10% during the first 10 years and up to 20% in total after 25 years. | PCS | 32 |  | 0
8 | Submersible Pump with long Cable 7.5 , 380 V , H= 70- 90 , Q=30- 40 m³/h ,Ø = 3"equipped with all necessary junctions. | PCS | 2 |  | 0
9 | MC4 Male and Female | PCS | 8 |  | 0
10 | Electric Cable DC 10 mm | M | 140 |  | 0
11 | Protection and installation of Protection box with suction fan with Fuse 1000 V, 100 Amp, size 40 CM X 60 CM | box | 2 |  | 0
12 | Provide and installation of Change Over Switch 100 Amp, Germany or India established | box | 2 |  | 0
13 | Provide and installation of Stand for Solar Panel ,Manufacture and assembly of steel solar panel holder for 16 panel use H section steel 12 inches for column with thickness 3-4 mm , It must be painted against rust and then painted purple. | Lum sum | 2 |  | 0
14 | Provide and installation of DC Junction Box with Circuit Breaker 100 Amp | box | 2 |  | 0
15 | supply UPVC or galvanized pipe 3 inches, 3 m long and carry out borehole installation the cost include all junctions and fittings, each borehole has 18 pipes | site | 2 |  | 0
| Sub Total for solar system supply and installation |  |  |  | 0
Water Yard protection fencing and room construction
16 | Supply materials (Gabain sheet 3.5mm thickness, Height 2 m, 25 cm fabrication), length 70 m, heavy Angular iron 3 mm thickness,3 inch size columns, cement, gravel, sand, Iron bar 12mm, tie wire, painting, and carry out the installation of fencing for area 20 m long *15 m wide, cut the heavy 2.5 m and fixed with concrete ratio 1:2:4 footing size (0.40m x 0.40m x 0.40m). and weld the corners supported heavy angle 1.2 m and fixed with interval of 2.5 m and apply the Gabain with full tightened with steel wire (2mm) at each 0.50m and diagonally between supports . supply iron bar 12 mm and welded horizontally three strips with interval of 0.6 m for four lines, ensure all engineering specification and SWC standard. | site | 2 |  | 0
17 | Supply a metallic angle heavy and cut it 0.5 m and weld it at the top of the distributed supported columns, 20 angles to be like V, and supply anti-rust galvanized protection wire with a diameter of 0.5 m and carry out the installation accordingly . | site | 2 |  | 0
18 | Supply materials (¾inch size gravel, clean sand, welding rod, and Corrugated Zinc 0.35 mm ) and carry out the repair of existing of control room 4m X 3 m X 3 m length, width and height respectively, and construct room platform 3m width*4m length with 0.07m thickness and ensure all engineering specification as per WSC. and supply and apply painting internally and externally as per engineer request. | room | 2 |  | 0
19 | Provide and installation of Main Gate height 1.80 m*length 3.50 m for water yard. Gate size (1.8m x 3.50m) consists of 2 liftslab filling is with steel sections 2x4cm vertically and horizontally each 20cm. Gate supports are from steel sections 5x10 cm fixed on plain concrete footing (0.50m x 0.50m x 0.60m). All steel sections must be painted with red-oxide paint and 2 coats of approved oil paint. | Lum sum | 2 |  | 0
20 | supply materials and install a sign board and fix it in the elevated tank and wall | signboard | 2 |  | 0
21 | Supply gravel and carry out the site levelling and apply the gravel on the top of the yards and carry out the site cleaning. | site | 2 |  | 0
22 | Site cleaning and finishing this is include removal and lawful disposal of all construction debris; thorough cleaning of floors, walls, rooms, fixtures, and services; minor touch-ups and rectifications; dismantling and removal of temporary works; final surface preparation, safety checks, and completion ready for inspection and handover. | site | 2 |  | 0
| Sub activity fencing and control room |  |  |  | 0
Total in Word SDG |  |  |  |  | 0
Exchange rate |  |  |  |  | 2620
Company/NGO/CBO Name:
Name of Director:
Signature and stamp
Date: